## Line Calculation
This calculation sheet is used to make first-order approximations of transmission line characteristics and costs when detailed project data are not available. It is typically applied in cases where potential new interconnections are being considered, or when only public information exists. Based solely on two key inputs — voltage level and line length — the tool estimates: - the total investment cost (including lines, substations, and compensation equipment), and - the available transfer capacity of the line. These estimates provide input assumptions for the Electricity Planning Model (EPM), which requires indicative transmission capacity and cost parameters for its capacity expansion and least-cost investment analyses.
Number of lines |  | 1 | Voltage (kV) | Overhead line cost (M$/km) | Substation cost (M$/poste) | Section cost | Compensation cost
Voltage | kV | 220 | 400 | 0.5 | 7.5 | 5 | 40
Line length | km | 300 | 220 | 0.35 | 4.5 | 3.5 | 40
SIL (Surge Impedance Loading) = zero reactive power capacity | MW | 196.625
K(L) (stability derating factor) = length-related stability factor |  | 1.2
Pstab (stability-limited transfer capacity) | MW | 235.95
Pavail (available transfer capacity) = actual available capacity | MW | 235.95
Overhead line cost | M$/km | 0.35
Number of substations | # | 2
Substation cost (average of one bay + substation extension) | M$/poste | 4.5
Number of sections |  | 0
Section cost | M$/section | 3.5
Number of compensation sites |  | 0
Compensation cost (SVC, STATCOM, or series compensation) | M$/site | 40
Overhead line cost | M$ | 105
Substation cost (average of one bay + extension) | M$ | 9
Section cost | M$ | 0
Compensation cost (SVC, STATCOM, or series compensation) | M$ | 0
Total line cost | M$ | 114
Total cost | M$ | 114
Available capacity | MW | 235.95